Specification—5.2kW Inverter

- 1.Product Pictures

- （to be confirmed）

- 2.Main Features

1、3.2-inch segment code screen;

- It can work without batteries;

- It can be paired with lithium iron phosphate battery packs (51.2VDC) and lead-acid batteries (48VDC);

- It supports Plug-and-Play WIFI Stick, and WiFi remote monitoring is optional;

- Pure sine wave output;

- 6. Power factor 1.0; It can be paired with lithium iron phosphate battery packs (51.2VDC) and lead-acid batteries (48VDC);

- It supports multiple output priorities: mains priority (default), SBU priority;

- It is equipped with an internal photovoltaic MPPT controller, which increase the charging efficiency by more than 20%, and the maximum photovoltaic input is 500Vdc;

- It has overcharge protection and over-discharge protection functions, which can safely ensure a longer battery life;

- It features intelligent exhaust and heat dissipation, intelligent overload protection, short-circuit protection and automatic alarm;

11、It has a detachable dust cover and can be used in harsh environments;

12、It can be used in parallel to form single-phase or three-phase output, with a maximum of 9 units that can be connected in parallel.

- 3.Technical Parameters

| Model | SP-5.2K-EP1 |  |  |
| --- | --- | --- | --- |
| Product Whole Part |  |  |  |
| Rated Output Power | 5200W/5200VA |  |  |
| Rated Output Voltage | 230VAC±5% |  |  |
| Rated Output Frequency | 50Hz/60Hz±1% |  |  |
| Off-grid/Grid Connected | Off-grid(NOT support grid-connected) |  |  |
| Operating Modes | Two modes: mains power mode(prior by default) and SBU mode. |  |  |
| Parallel Operation Function (Inverter) | Up to 9 units can be connected in parallel, and they can be connected in single phase or three-phase |  |  |
| Parallel Interface | YES(DB15 Interface) |  |  |
| Diesel Power Generation | Supported |  |  |
| Diesel Generator Dry Contacts | Diesel generator dry contacts: 2 paths reserved(1NC，1NO) |  |  |
| Inverter Part |  |  |  |
| Inverter Technical Route | High-frequency solution |  |  |
| Unidirectional/Bidirectional(Inverter) | Bidirectional |  |  |
| Rated Output Power | 5200W/5200VA Continuous |  |  |
| Peak Power | 10400VA/10400W，Duration：240ms |  |  |
| Overload Capacity | ≥150%load@5s;110%~150%load@10s |  |  |
| Rated Output Voltage | In inverter mode：230VAC±5% In the bypass mode of mains power: consistent with the input mains power |  |  |
| Output Frequency | In inverter mode：50Hz/60Hz±1% In the bypass mode of mains power: consistent with the input mains power |  |  |
| AC Output Interface | Through-the-Wall terminal: 1 Set, 3P（L、N、PE） |  |  |
| Maximum Inverter Efficiency | 90-94% |  |  |
| Stand-by Power Consumption | <20W |  |  |
| AC Input Part |  |  |  |
| AC Input Rated Voltage | 230Vac |  |  |
| AC Input Voltage Range | APL:90Vac～280Vac±7V UPS:170Vac~280Vac±7V |  |  |
| Rated frequency of AC Input | 50/60Hz（Automatic detection） |  |  |
| Frequency Range of AC Input | 40～65Hz±1Hz |  |  |
| AC Input Interface | Through-the-Wall terminal: 1 Set, 3P（L、N、PE） |  |  |
| AC Charging Derating | For 170VAC and above, the output is at full capacity. For 170VAC and below, linear derating begins. For 90VAC, it is 30% to 50% |  |  |
| Maximum Charging Current of AC | 80A |  |  |
| Maximum Bypass Overload Current | 40A |  |  |
| Fast Charging | Not supported(But the charging current can be set) |  |  |
| Battery Part |  |  |  |
| Battery Voltage Platform | 48VDC |  |  |
| Voltage Points for Battery Pack Charging/Discharging (Configurable) |  |  |  |
|  | Lithium iron phosphate battery (16 strings) | Lithium iron phosphate battery (15 strings) | Lead-acid battery (24 strings) |
| Battery Charging Cut-off voltage | 58.4VDC | 54.8VDC | 63VDC |
| Battery Charging Alarm Voltage | 57.6VDC | 54VDC | 63VDC |
| Battery Discharge Recovery Voltage | 45VDC | 42.2VDC | 41.1VDC |
| Battery Discharging Cut-off voltage | 42VDC | 39.4VDC | 40.6VDC |
| Battery Shutdown Voltage | 40VDC | 37.5VDC | 39.6VDC |
| Battery pack Voltage Accuracy | ±0.3%(To be confirmed after testing) |  |  |
| Maximum Current for Hybrid Charging | AC+PV(100A) |  |  |
| PV Input Part |  |  |  |
| Maximum Power of PV charging | 6000W |  |  |
| Maximum PV Open-Circuit Voltage | 500V |  |  |
| MPPT Voltage Range | 100-450VDC |  |  |
| PV Voltage Accuracy | ±2V |  |  |
| MPPT Channel | 1 Channel |  |  |
| MPPT Currency Range | 0~18A |  |  |
| Maximum MPPT Efficiency | >99% |  |  |
| PV Input Interface | Through-the-Wall terminal |  |  |
| The Rated Voltage for PV Charging the Battery | Configurable: Lithium iron phosphate battery (16 strings) mode: 58.4V Configurable: Lithium iron phosphate battery (15 strings) mode: 54.75V Configurable: Lead-acid battery (24 strings) mode: 57.6V |  |  |
| Rated Maximum Charging Current for the Battery | 100A |  |  |
| Protective Function |  |  |  |
| For fault/alarm function | Please refer to the fault code and alarm code |  |  |
| Display Screen |  |  |  |
| Display Screen Size | 3.2 inches |  |  |
| Display Screen Type | Ordinary segment code screen |  |  |
| Button + Indicator Light |  |  |  |
| Inverter On/Fff Button | Rocker switch |  |  |
| Reset Button | Non-optional |  |  |
| Screen Buttons | 4(ESC、DOWN、UP、ENTER) |  |  |
| Indicator Light | 3(AC OUT、CHARGE、FAULT) |  |  |
| Communication Function |  |  |  |
| Communication Interface | - 1 RJ45 interface: including RS485 protocol (BMS communication),CAN protocol (BMS communication),RS232 (Upper Computer Communication - 1 DB15 interfaces, 1 male and 1 female: CAN+ synchronization signal, used for parallel communication - 2 Current-sharing interfaces: used for current-sharing detection during parallel operation - 1 USB interface: RS232 protocol, used for WIFI stick communication interface - 2 Dry contacts: used for connecting diesel generators |  |  |
| WIFI Communication Function (optional) | Supported |  |  |
| WIFI Stick（optional） | External WIFI stick (USB interface, RS232 protocol, 5VDC power supply) |  |  |
| APP Functions (optional) | It can be connected to the mobile phone APP to check the working status of the inverter and control its on and off |  |  |
| Other Parameters |  |  |  |
| Noise | ≤55dB |  |  |
| IP Rating | IP21 |  |  |
| Shell Material | Sheet metal |  |  |
| Wiring Compartment | YES |  |  |
| Operating Ambient Temperature | -10℃～+50℃ |  |  |
| Storage Ambient Temperature | -15℃～+60℃ |  |  |
| Relative Humidity | 5%~95%（No condensation） |  |  |
| Heat Dissipation Method | Forced air cooling |  |  |
| Altitude | 4000m（＞3000m Start derating） |  |  |
| Product Dimensions:Width*Depth*Height（mm） | 420x325x138 mm |  |  |
| Packaging Size：Width*Depth*Height（mm） | to be confirmed |  |  |
| Weight | 10.9kG |  |  |
| Installation Method | Wall-mounted |  |  |
| Other Descriptions |  |  |  |
| Positioning | Mid-to-low range market |  |  |
| Certification | For now, it's not necessary. If certification is required, we can purchase the certificate or make another prototype that can pass the certification. |  |  |
| Warranty | 1 Year |  |  |
| Grounding Point | YES |  |  |